## Inst Amp1 Calc
Circuit Calc - Inst Amp1
Calculate Gains, Levels, Sensitivities |  |  |  |  | Enter values
Calc results
AN-539, APPLICATION NOTE, Analog devices
Components & Parameters
Circuit Block | Name | Inst Amp1
Supply | Vcc | 5
Wheatstone Bridge | R1 | 350 | ohms
| R2 | 350 | ohms
| R3 | 350 | ohms
| R4 | 350 | ohms
Inst Amp | RG_int | 100000 | internal gain resistor
| RG_ext | 1130 | external gain resistor
Input Node | vin | vp-vn
Output Node | vo | vo
Signal Gain | K | 89.4956 | vo/vin = Rg_int/Rg_ext + 1
Signal Levels | vin_FS | 0.02 | Input Full-Scale
| vout_FS | 1.7899 | Output Full-Scale
V common mode | vcm | 2.5 | Vcc*R2/(R1+R2)
OFFSET SENSITIVITY
S (How does each error source contribute to error at Analysis Node)
Input Errors | S, Analysis Node
voff, vnoise | S, vp | 1 | V/V | S = vp /voff = 1
Ib | S, (vp-vn) | 0 | V/A | S = (vp-vn)/ib =( R1¦¦R2 - R3¦¦R4 )
Iboff | S, (vp-vn) | 175 | V/A | S = (vp-vn)/iboff =1/2*( R1¦¦R2 + R3¦¦R4 )
Vcmr | S, vp | 1 | V/V | S = vp/Vcmr = 1
Output Errors
voff_vo | S, vo | 1 | V/V | S = vo /voff_vo = 1
nonlin_vo | S, vo | 1 | V/ppm | S = vo/vnonlin_vo = 1
`
GAIN SENSITIVITY
S (How does each error source contribute to a signal Gain error)
K = vo/vs Signal Gain
S =(ΔK/K)/(ΔR/R) Sensitivity of K to a change in R
S = 0.5% means that a 1% change in the device causes a 0.5% change in the signal gain.
RG_int | K | 89.4956 |  | RG_int/RG_ext + 1 |  | K is the circuit gain
| K' | 90.3805 |  | K( RG_int*1.01 ) |  | K' is the gain with a 1% resistor tolerance used to calculate sensitivity S.
| S | 0.98883 |  | ((K'-K)/K) / 0.01 |  | S = (ΔK/K) / (ΔR/R) = ((K'-K)/K) / 0.01
RG_ext | K | 89.4956 |  | RG_int/RG_ext + 1
| K' | 88.6194 |  | K( RG_ext*1.01 )
| S | -0.97904 |  | ((K'-K)/K) / 0.01
Note on C36: The voltage at each input node is calculated as vp = ib * Ra¦¦Rb vn = ib * Rc¦¦Rd therefore vp - vn = ib*(Ra¦¦Rb - Rc¦¦Rd) S = (vp-vn)/ib = Ra¦¦Rb - Rc¦¦Rd
Note on C38: The voltage at each input node is calculated as vp = iboff/2 * Ra¦¦Rb vn = -iboff/2 * Rc¦¦Rd therefore vp - vn = iboff/2*(Ra¦¦Rb+Rc¦¦Rd) S = (vp-vn)/iboff = 1/2*(Ra¦¦Rb+Rc¦¦Rd)

## Offset Errors
Offset Errors - Inst Amp
Enter values
Calc results
SPECIFICATIONS AND RESULTS
| Source Full Scale | Temp Change
| Vs_FS | ΔT
| 0.02 | 60
| Accuracy Spec | Error Budget Analysis |  |  | PASS if > 0
Offset Error | Error (V) | Initial Error | Drift Error | Total Error | Margin % | P/F ?
Referred to Input | 0.0002 | 0.00012 | 6.9741e-05 | 0.00018974 | 5.1316 | PASS
|  |  |  | 9486.8445 | ppm
OFFSET ERRORS
Initial Errors |  | Error Source | Error Value |  | Analysis Node | Offset Sensitivity | Offset Error at Analysis Node | Gain from input to analysis node | Offset Error RTI (V) |  |  | Worst Case Sum | Roor Sum Square
Circuit Block | Ref, Part | e | e | unit | Va | S | ΔVoffset = e*S (V) | Ka = Va/vin | ΔVoffset_rti = ΔVo / Ka | ppm |  | abs(ΔVoffset_rti) | Δvoffset_rti^2
Inst Amp1 | U1, AD623b | voff | 0.0001 | V | vs | 1 | 0.0001 | 1 | 0.0001 | 5000 |  | 0.0001 | 1e-08
" | U1, AD623b | voff_vo | 0.0005 | V | vo | 1 | 0.0005 | 89.4956 | 5.5869e-06 | 279.3434 |  | 5.5869e-06 | 3.1213e-11
" | U1, AD623b | ib | 2.5e-08 | A | vs | 0 | 0 | 1 | 0 | 0 |  | 0 | 0
" | U1, AD623b | iboff | 2e-09 | A | vs | 175 | 3.5e-07 | 1 | 3.5e-07 | 17.5 |  | 3.5e-07 | 1.225e-13
" | U1, AD623b | Vcm/CMRR | 1.4059e-05 | V/V | vs | 1 | 1.4059e-05 | 1 | 1.4059e-05 | 702.9267 |  | 1.4059e-05 | 1.9764e-10
end
[10 empty] | WC |  | WCA Total | RSS Total
[10 empty] | 5999.7701 | V | 0.00012 | 0.00010114
Drift, Other Errors |  | Error Source | Error Value |  | Analysis Node | Offset Sensitivity | Offset Error at Analysis Node | Gain from input to analysis node | Offset Error RTI (V) |  |  | Worst Case Sum | Roor Sum Square
Circuit Block | Ref, Part | e | e | unit | Va | S | ΔVoffset = e*ΔT*S (V) | Ka = Va/vin | ΔVoffset_rti = ΔVo / Ka | ppm |  | abs(ΔVoffset_rti) | Δvoffset_rti^2
Inst Amp1 | U1, AD623b | voff_TC | 1e-06 | V/C | vs | 1 | 6e-05 | 1 | 6e-05 | 3000 |  | 6e-05 | 3.6e-09
" | U1, AD623b | voff_vo_TC | 1e-05 | V/C | vo | 1 | 0.0006 | 89.4956 | 6.7042e-06 | 335.2121 |  | 6.7042e-06 | 4.4947e-11
" | U1, AD623b | ib_TC | 2.5e-11 | A/C | vs | 0 | 0 | 1 | 0 | 0 |  | 0 | 0
" | U1, AD623b | iboff_TC | 5e-12 | A/C | vs | 175 | 5.25e-08 | 1 | 5.25e-08 | 2.625 |  | 5.25e-08 | 2.7563e-15
" | U1, AD623b | vnoise | 7.5e-07 | Vp | vs | 1 | 7.5e-07 | 1 | 7.5e-07 | 37.5 |  | 7.5e-07 | 5.625e-13
" | U1, AD623b | vnonlin_vo | 0.0002 | V | vo | 1 | 0.0002 | 89.4956 | 2.2347e-06 | 111.7374 |  | 2.2347e-06 | 4.9941e-12
end
[10 empty] | WC |  | WCA Total | RSS Total
[10 empty] | 3487.0745 | V | 6.9741e-05 | 6.0419e-05
Note on C12: Get the total error from Worst Case Analysis (WCA). Change to Root Sum Square (RSS) total error if desired.
Note on C28: Insert rows for new parts above the "end" row. Pie Charts and Totals will automatically include new part.
Note on C41: Insert rows for new parts above the "end" row. Pie Charts and Totals will automatically include new part.
Note on D12: Get the total error from Worst Case Analysis (WCA). Change to Root Sum Square (RSS) total error if desired.
Note on D27: Get CMRR (dB) spec from datasheet Get Vcm from Calc sheet Vcmr = Vcm/10^(CMRR/20)
Note on D39: Vpp causes a max error of Vp = Vpp/2 Ex: Vp = 1.5uVpp / 2 = 0.75uVp
Note on D40: Get Vnonlin from datasheet given in ppm at Vomax and specific K. Vnonlin = NONLIN(ppm) * 1e-6 * Vomax = 50ppm * 1e-6 * 4V (at K=100)
Note on E12: Total Error = Initial Error + Drift Error
Note on F12: Design Margin = (Total_Err - Spec_Err) / Spec_Err * 100%
Note on G22: Get Sensitivity S calculated in CIRCUIT CALC sheet.
Note on G34: Get Sensitivity S calculated in CIRCUIT CALC sheet.
Note on M29: Sum total error as Worst Case Analysis WCA = ¦err1¦+¦err2¦+...
Note on M42: Sum total error as Worst Case Analysis WCA = ¦err1¦+¦err2¦+...
Note on N29: Sum total error as Root Sum Square RSS = sqrt( err1^2 + err2^2 + ...)
Note on N42: Sum total error as Root Sum Square RSS = sqrt( err1^2 + err2^2 + ...)

## Gain Errors
Gain Errors - Inst Amp
Enter values
Calc results
SPECIFICATIONS AND RESULTS
Temp Change
ΔT
60
| Accuracy Spec | Error Budget Analysis |  |  | PASS if > 0
Gain Error | Error (%) | Initial Error | Drift Error | Total Error | Margin % | P/F ?
| 1 | 0.44399 | 0.35539 | 0.79938 | 20.0617 | PASS
|  |  |  | 7993.8282 | ppm
GAIN ERRORS
Initial Errors |  | Error Source | Error Value |  | Analysis Node | Gain Sensitivity | Offset Error at Analysis Node |  | Normalized gain errors scale directly to input
Block | Ref, Part | e | e | unit | Va | S | ΔK/K = e*S (%) | ppm | abs(ΔK/K) | (ΔK/K)^2
Inst Amp1 | RG_int, AD623 | RG_int Tol | 0.35 | % | vo | 0.98883 | 0.34609 | 3460.8919 | 0.34609 | 0.11978 | %
" | RG_ext, 0.1%, 10ppm/C | Rg_ext Tol | 0.1 | % | vo | -0.97904 | -0.097904 | -979.0359 | 0.097904 | 0.0095851 | %
end
[8 empty] | WC | WCA Total | RSS Total
[8 empty] | 4439.9278 | 0.44399 | 0.35967
Drift, Random Errors |  |  |  |  | Analysis Node | Gain Sensitivity | Offset Error at Analysis Node |  | Normalized gain errors scale directly to input
Block | Ref, Part | Component | e | unit | Va | S | ΔK/K = e*ΔT*S (%) | ppm | abs(ΔK/K) | (ΔK/K)^2
Amp 1 | RG_int, AD623 | RG_int TC | 50 | ppm/C | vo | 0.98883 | 0.29665 | 2966.4788 | 0.29665 | 0.088 | %
" | RG_ext, 0.1%, 10ppm/C | Rg_ext TC | 10 | ppm/C | vo | -0.97904 | -0.058742 | -587.4215 | 0.058742 | 0.0034506 | %
end
[8 empty] | WC | WCA Total | RSS Total
[8 empty] | 3553.9003 | 0.35539 | 0.30241
Note on C12: Get the total error from Worst Case Analysis (WCA). Change to Root Sum Square (RSS) total error if desired.
Note on C25: Insert rows for new parts above the "end" row. Pie Charts and Totals will automatically include new part.
Note on C34: Insert rows for new parts above the "end" row. Pie Charts and Totals will automatically include new part.
Note on D12: Get the total error from Worst Case Analysis (WCA). Change to Root Sum Square (RSS) total error if desired.
Note on E12: Total Error = Initial Error + Drift Error
Note on F12: Design Margin = (Total_Err - Spec_Err) / Spec_Err * 100%
Note on G22: Get Sensitivity S calculated in CIRCUIT CALC sheet.
Note on G31: Get Sensitivity S calculated in CIRCUIT CALC sheet.
Note on L26: Sum total error as Worst Case Analysis WCA = ¦err1¦+¦err2¦+...
Note on L35: Sum total error as Worst Case Analysis WCA = ¦err1¦+¦err2¦+...
Note on M26: Sum total error as Root Sum Square RSS = sqrt( err1^2 + err2^2 + ...)
Note on M35: Sum total error as Root Sum Square RSS = sqrt( err1^2 + err2^2 + ...)